## Sheet1
Component | Probability of Failure | Failure Time | Number | Comments | Item | Condition Index
XCEL Energy (Commercial Power) | 0.99984 | 0 | 0 | Said to fail only an hour every other month | Calculated | 77
Generator 1 | 0.99998 | 6 | 1 | Need info from engineers | 118 | 84
Generator 2 | 0.99997 | 6 | 2 | Need info from engineers | 118 | 77
Generator 3 | 0.99999 | 6 | 3 | Need info from engineers | 118 | 93
Generator 4 | 1 | 6 | 4 | Need info from engineers | 118 | 100
Comercial Bus | 1 | 0 | 5 | Set to 100% since from the meeting, the likely hood of the bus failing is highly unlikely. If it was to fail, the system would be down for a very long time. This kind of failure is unpredictable. |  | 95
Generator Bus | 1 | 0 | 6 | Set to 100% since from the meeting, the likely hood of the bus failing is highly unlikely. If it was to fail, the system would be down for a very long time. This kind of failure is unpredictable. |  | 79
SS UPS 1 | 1 | 0 | 7 | Need info from engineers | 213 | 91
SS UPS 2 | 1 | 0 | 8 | Need info from engineers | 213 | 81
Swichgear Input 1 | 1 | 8 | 9 | Need info from engineers | 195 | 94
Swichgear Input 2 | 1 | 37 | 10 | Need info from engineers | 196 | 98
UPS 1B | 1 | 0 | 11 | Need info from engineers | 213 | 71
UPS 1A | 1 | 0 | 12 | Need info from engineers | 213 | 78
UPS 2B | 1 | 0 | 13 | Need info from engineers | 213 | 74
UPS 2A | 1 | 0 | 14 | Need info from engineers | 213 | 91
UPS 1 Switchboard | 1 | 2 | 15 | Need info from engineers | 183 | 99
UPS 2 Switchboard | 1 | 2 | 16 | Need info from engineers | 183 | 88
STS 2 | 1 | 3 | 17 | Unknown |  | 99
Switchgear Output 2 | 1 | 8 | 18 | Need info from engineers | 195 | 76
Critical bus 2A | 1 | 0 | 19 | Set to 100% since from the meeting, the likely hood of the bus failing is highly unlikely. If it was to fail, the system would be down for a very long time. This kind of failure is unpredictable. |  | 87
Critical bus 2B | 1 | 0 | 20 | Set to 100% since from the meeting, the likely hood of the bus failing is highly unlikely. If it was to fail, the system would be down for a very long time. This kind of failure is unpredictable. |  | 78
Panel TB12A-TB3 | 1 | 1 | 21 | Need info from engineers | 130 | 73
PDU-B | 0.99998 | 0 | 22 | Unknown |  | 75
PDU-A | 1 | 0 | 23 | Unknown |  | 98
STS | 0.99999 | 0 | 24 | Unknown |  | 88
Panel | 1 | 1 | 25 | Need info from engineers | 130 | 88
Panel DPA | 1 | 1 | 26 | Need info from engineers | 130 | 82
Trans T4 | 1 | 26 | 27 | Unknown Item | 131 | 99
Panel LPA 1 | 1 | 21 | 28 | Need info from engineers | 132 | 79
Panel LPA 2 | 0.99999 | 21 | 29 | Need info from engineers | 133 | 71
Water Tower 1 | 0.99878 | 20 | 30 | Need info from engineers | 94 | 79
Pump 1 | 0.99999 | 7 | 31 | Need info from engineers | 163 | 95
Water Tower 2 | 0.99907 | 20 | 32 | Need info from engineers | 94 | 84
Pump 2 | 0.99998 | 7 | 33 | Need info from engineers | 163 | 84
Water Tower 3 | 0.99895 | 20 | 34 | Need info from engineers | 94 | 82
Pump 3 | 0.99999 | 7 | 35 | Need info from engineers | 163 | 93
Sump | 1 | 0 | 36 | Unknown, Assumed 1 because of needs |  | 70
Chiller 2 | 0.99996 | 10 | 37 | Need info from engineers | 57 | 94
Chiller 1 | 0.99997 | 10 | 38 | Need info from engineers | 57 | 96
Chiller 3 | 0.9999 | 10 | 39 | Need info from engineers | 57 | 85
Chiller 6 | 0.99988 | 10 | 40 | Need info from engineers | 57 | 83
Chiller 5 | 0.99981 | 10 | 41 | Need info from engineers | 57 | 72
Chiller 4 | 0.9999 | 10 | 42 | Need info from engineers | 57 | 85
Pump P3 | 0.99998 | 7 | 43 | Need info from engineers | 163 | 83
Pump P4 | 0.99998 | 7 | 44 | Need info from engineers | 163 | 81
CW Storage Tank | 1 | 1 | 45 |  | 199 | 77
Pump P5 | 0.99998 | 7 | 46 | Need info from engineers | 163 | 84
Pump | 0.99997 | 7 | 47 | Need info from engineers | 163 | 75
CRAH 1 | 0.99998 | 2 | 48 | Need info from engineers | 6 | 86
CRAH 2 | 0.99999 | 2 | 49 | Need info from engineers | 6 | 89

## Sheet2
| CI | CI Set | Original Prob | New Prob | new prob set
XCEL Energy (Commercial Power) | 95 | 77 | 0.99932 | 0.99984 | 0.99984
Generator 1 | 99 | 84 | 0.99987 | 0.99998 | 0.99998
Generator 2 | 97 | 77 | 0.99987 | 0.99997 | 0.99997
Generator 3 | 100 | 93 | 0.99987 | 0.99999 | 0.99999
Generator 4 | 96 | 100 | 0.99987 | 1 | 1
Comercial Bus | 84 | 95 | 1 | 1 | 1
Generator Bus | 95 | 79 | 1 | 1 | 1
SS UPS 1 | 75 | 91 | 1 | 1 | 1
SS UPS 2 | 98 | 81 | 1 | 1 | 1
Swichgear Input 1 | 96 | 94 | 1 | 1 | 1
Swichgear Input 2 | 89 | 98 | 1 | 1 | 1
UPS 1B | 81 | 71 | 1 | 1 | 1
UPS 1A | 91 | 78 | 1 | 1 | 1
UPS 2B | 81 | 74 | 1 | 1 | 1
UPS 2A | 74 | 91 | 1 | 1 | 1
UPS 1 Switchboard | 87 | 99 | 0.99999 | 1 | 1
UPS 2 Switchboard | 91 | 88 | 0.99999 | 1 | 1
STS 2 | 100 | 99 | 0.9999 | 1 | 1
Switchgear Output 2 | 79 | 76 | 1 | 1 | 1
Critical bus 2A | 84 | 87 | 1 | 1 | 1
Critical bus 2B | 92 | 78 | 1 | 1 | 1
Panel TB12A-TB3 | 86 | 73 | 0.99998 | 1 | 1
PDU-B | 85 | 75 | 0.9999 | 0.99998 | 0.99998
PDU-A | 95 | 98 | 0.9999 | 1 | 1
STS | 83 | 88 | 0.9999 | 0.99999 | 0.99999
Panel | 97 | 88 | 0.99998 | 1 | 1
Panel DPA | 74 | 82 | 0.99998 | 1 | 1
Trans T4 | 97 | 99 | 0.9999 | 1 | 1
Panel LPA 1 | 97 | 79 | 0.99998 | 1 | 1
Panel LPA 2 | 86 | 71 | 0.99998 | 0.99999 | 0.99999
Water Tower 1 | 99 | 79 | 0.99418 | 0.99878 | 0.99878
Pump 1 | 87 | 95 | 0.9999 | 0.99999 | 0.99999
Water Tower 2 | 87 | 84 | 0.99418 | 0.99907 | 0.99907
Pump 2 | 92 | 84 | 0.9999 | 0.99998 | 0.99998
Water Tower 3 | 90 | 82 | 0.99418 | 0.99895 | 0.99895
Pump 3 | 82 | 93 | 0.9999 | 0.99999 | 0.99999
Sump | 96 | 70 | 1 | 1 | 1
Chiller 2 | 72 | 94 | 0.99931 | 0.99996 | 0.99996
Chiller 1 | 95 | 96 | 0.99931 | 0.99997 | 0.99997
Chiller 3 | 79 | 85 | 0.99931 | 0.9999 | 0.9999
Chiller 6 | 72 | 83 | 0.99931 | 0.99988 | 0.99988
Chiller 5 | 98 | 72 | 0.99931 | 0.99981 | 0.99981
Chiller 4 | 79 | 85 | 0.99931 | 0.9999 | 0.9999
Pump P3 | 82 | 83 | 0.9999 | 0.99998 | 0.99998
Pump P4 | 84 | 81 | 0.9999 | 0.99998 | 0.99998
CW Storage Tank | 76 | 77 | 0.99999 | 1 | 1
Pump P5 | 83 | 84 | 0.9999 | 0.99998 | 0.99998
Pump | 91 | 75 | 0.9999 | 0.99997 | 0.99997
CRAH 1 | 85 | 86 | 0.99988 | 0.99998 | 0.99998
CRAH 2 | 86 | 89 | 0.99988 | 0.99999 | 0.99999